DC-T6831WRA

Architectural and Engineering Specifications

Version 1.0.1

PART 1: PLEASE REFER TO ATTACHED DOCUMENTS - OVERVIEW & FORMAT SAMPLES

PART 2: PRODUCTS

Division 28 – Electric Safety and Security

Level 1 - 28.20.00 – Video Surveillance

Level 2 - 28.21.00 – Surveillance Cameras

Level 3 - 28.21.13 – IP Cameras

Manufacturer

- IDIS Co., Ltd.
IDIS Tower, 344 Pangyo-ro, Bundang-gu
Seongnam-si, Gyeonggi-do, 13493, Korea
Tel: 	+82 31 723 5400
Fax: 	+82 31 723 5100

General

Product Description

The DC-T6831WRA is a high-performance 8MP Edge AI Plus bullet camera designed for professional surveillance applications. It is NDAA and TAA compliant and features a motorized vari-focal lens (4.3–9.8mm). The camera supports H.264, H.265, and Motion JPEG (MJPEG) compression with IDIS Intelligent Codec for efficient bandwidth and storage management.

True WDR up to 120dB and built-in IR illumination up to 60m (196.9ft) provide clear imaging under challenging lighting conditions. Integrated IDIS Deep Learning Analytics (IDLA and IDLA Pro) support advanced object detection and classification, including human, vehicle, and face attributes. Smart Failover enables local recording on microSD cards up to 512GB during network interruptions.

With IK10 vandal resistance and IP67/NEMA 4X environmental protection, the camera is suitable for demanding indoor and outdoor environments. It supports ONVIF Profile S, T, and M, seamless integration with IDIS DirectIP NVRs, two-way audio, alarm input/output, and 12V DC or PoE (IEEE 802.3af Class 3) power..

General Specification

- The IP camera shall be equipped with 8 Megapixel 1/1.8" CMOS Sensor(3840 x 2160).

- The IP camera shall be equipped with 4.3 ~ 9.8mm motorized Vari-focal lens, F1.6 ~ F2.6.

- The IP camera shall be a true day/night camera with a mechanical filter (ICR) for enhanced low light performance.

- The IP camera shall support True Wide Dynamic Range (WDR) for improved image clarity in high-contrast scenes (120 dB).

- The IP camera shall be equipped with 6 Infrared LEDs with a range up to 60m (196.9ft).

- The camera shall support P-Iris for better image clarity under varying lighting conditions.

- The IP camera shall support 2DNR and 3DNR (Dynamic Noise Reduction) to reduce image noise and optimize storage and bandwidth usage.

- The camera shall be enclosed in a vandal-resistant housing rated IK10, with IP67 and NEMA 4X environmental protection.

- The camera shall have a 10/100Base-T RJ-45 Ethernet port with auto-sensing and full/half-duplex mode.

- The camera shall support 12VDC power input (1.1A, 13.2W) and Power over Ethernet (PoE) IEEE 802.3af Class 3 (57VDC, 12W).

- The camera shall include a CVBS video output (NTSC/PAL) for local setup and testing.

- The IP camera shall be equipped with an on-board microSD/SDHC/SDXC card slot, supporting up to 512GB for edge recording.

- The camera shall support IDIS NLTSrec (Non-Linear Time Shifting recording) technology with 60MB buffer memory, to prevent data loss during short network interruptions or recorder overload.

- The camera shall support a maximum resolution of 3840 x 2160 at rates up to 30ips (images per second).

- The IP camera shall provide network connection using H.265, H.264 and MJPEG** compression.

- The IP camera shall support quadruple streams in DirectIP 2.0 protocol mode.

- The IP camera shall conform to the ONVIF Profile S/T/M.

- The IP camera shall be equipped with embedded web server (IDIS Web) which works independently using a Web Browser with ActiveX plug-in.

- The IP camera shall include security features such as: FIPS 140-3 Level 3, Digest authentication, Password Protection, Brute force delay protection, User access log, IP Filtering, IEEE802.1x(EAP-TLS), Chained Fingerprint, SSL Encryption, HTTPS Encryption for greater security.

- The IP camera shall support bandwidth limitation and MAT (Multi-streaming Adaptive Transmission) for optimized network usage.

- The IP camera shall have Easy network access via UPnP (Universal Plug and Play) function and embedded mDNS (Multicast DNS) protocol.

- The IP camera shall have Intelligent Video Analytics, including:

- A-cut Support

- Object Metadata: Human, Vehicle, Face

- Object Attribute: Human[Gender, Age, Bag, Hat, Colors], Vehicle[Car, Truck, Bus, Bike(Bicycle, Motorcycle), ETC, Colors], Face[Gender, Age, Glasses, Hat, Mask]

- IDLA: Object Detection, Intrusion, Loitering, Line Crossing, Face Detection

- IDLA Pro: Crowd Detection, Abandoned Object Detection, Removed Object Detection, Fall Detection

- Basic: Video Motion Detection, Active Tampering Alarm

Protocol Specification: DirectIP 2.0

- The IP camera shall have DirectIP 2.0 mode.

- DirectIP 2.0 protocol shall provide easy connection to DirectIP NVR for automatic discovery and video streaming configuration.

- DirectIP 2.0 shall provide the compatibility with IDIS Solution Suite VMS or ONVIF for third-party software solutions.

- DirectIP 2.0 shall support camera can be linked to IDIS software solution such as IDIS Center and IDIS Solution Suite, or 3rd party solution while it is being connected to a DirectIP NVR.

- DirectIP 2.0 camera shall be compatible with DirectIP 1.0 NVR as well as DirectIP 2.0 NVR.

- DirectIP 2.0 camera shall be unavailable for No-password login when connecting to DirectIP 2.0 NVR and IDIS Software Solutions.

- DirectIP 2.0 protocol shall provide Quadruple streams.

- DirectIP 2.0 protocol shall support H.264 and H.265 and MJPEG compression.

Technical Specification

Video Specification

- Image Sensor: 1/1.8" CMOS

- Maximum Resolution: 3840 x 2160

- Scanning Mode: Progressive Scan

- Lens Type: Motorized Vari-focal (f=4.3 ~ 9.8mm, F1.6 ~ F2.6)

- Iris Control: P-Iris

- Angular Field of View (H: Horizontal, V: Vertical, D: Diagonal):

  - Wide : 110.4º(H) 57.8º(V) 133.8º(D)

  - Tele : 45º(H) 25.2º(V) 51.8(D)

- Minimum Illumination:

  - COLOR : 0.13 lux @ F1.6

  - B/W : 0 lux  (IR LED ON)

- S/N Ratio: More than 45 dB

- Maximum Frame Rate: 30ips: 3840 x 2160(WDR)

- Video Resolution: 3840 x 2160, 1920 x 1080, 1280 x 720, 640 x 360

- Video Compression: H.265, H.264, MJPEG

- Video Compression Level: 4 levels: Basic, Standard, High, Very High

- Intelligent Codec is supported.

- Multi-Video Streaming: Quadruple streams

- Dynamic Range: 120dB

- True Day & Night: Yes (ICR)

- IR Distance (The number of LEDs, IR wavelength): 60m / 196.9ft (6ea)

- Image Stabilizer: Yes(EIS)

- Privacy Masking: 8 Zones

- Intelligent Video Analytic:

A-cut Support

Object Metadata: Human, Vehicle, Face

Object Attribute: Human[Gender, Age, Bag, Hat, Colors], Vehicle[Car, Truck, Bus, Bike(Bicycle, Motorcycle), ETC, Colors], Face[Gender, Age, Glasses, Hat, Mask]

IDLA: Object Detection, Intrusion, Loitering, Line Crossing, Face Detection

IDLA Pro: Crowd Detection, Abandoned Object Detection, Removed Object Detection, Fall Detection

Basic: Video Motion Detection, Active Tampering Alarm

- Video Out: 1 CVBS

Audio Specification

- Audio Compression Algorithm: Opus 16K/24K/48K, ADPCM 16K, G.726, G.711 a-Law/u-Law

- Audio Input / Output: Line-in 1ea / Line-out 1ea

- Two-way Audio Communication: Yes

- Pre-recorded Voice Alert(Audio Alarm): Yes

Network Specification

- Port: RJ-45 10/100 Base-T 1 port

- Network Protocols: DirectIP 2.0 Protocol, IPv4, IPv6, RTP/RTSP/TCP, RTP/RTSP/HTTP/TCP,

RTP/UDP RTSP/TCP, HTTP, HTTPS, FTP, SNTP, SMTP, FEN, mDNS, uPNP, SNMPv2

- Streaming Mode: Quadruple Streaming

Security Specification

- FIPS 140-3 Level 3, Digest authentication, Password Protection, Brute force delay protection, User access log, IP Filtering, IEEE802.1x(EAP-TLS), Chained Fingerprint, SSL Encryption, HTTPS Encryption

- Maximum Concurrent Sessions: 10 sessions shared across Admin, Watch, and Search, with a maximum of 1 Search session

Alarm and Event Specification

- Alarm Input / Output: 1 / 1

  - Alarm Input: 1 TTL, NC/NO Programmable, 4.3V(NC) or 0.3V(NO) threshold, 5V DC

  - Mechanical or electrical switches can be wired to the Alarm-In and GND connectors. The maximum voltage should not exceed 5V.

  - Alarm Output: 1 TTL open collector, 30mA @ 5 VDC

- Trigger Events: Motion Detection, Alarm in, Audio detection, Tampering, Object Detection, Intrusion, Loitering, Line Crossing, Face Detection, Crowd detection, Abandoned object detection, Removed object detection, Fall detection

- Event Notification: Remote S/W, Email (with Image)

Environmental Specification

- Operating Temperature: -40°C ~ +55°C (-40°F ~ +131°F)

*Starting up at above -20°C (-4°F)

- Operating Humidity: 0% to 90%

- Vandal-proof Enclosure: IK10

- Outdoor Ready: IP67, NEMA4X

Electrical Specification

- Power Source: 12VDC, PoE, IEEE 802.3af(Class 3)

- Power Consumption: 12VDC, 1.1A, 13.2W / PoE, IEEE 802.3af(Class3), 57VDC, 12W

- Regulatory Approvals: UL, FCC, CE, KC

Mechanical Specification

- Dimensions: 89.3mm X 89.3mm X 307.1mm (3.52" x 3.52" x 12.09")

- Unit Weight: 1.95kg (4.30lb)

Version History

| Version | Writer | Revision Date | Remarks |
| --- | --- | --- | --- |
| 1.0.1 | TS Team | Oct. 14. 2026 | Updated incorrect specs |
| 1.0 | TS Team | May. 30. 2025 | Initial Release |