DC-D4538RA

Architectural and Engineering Specifications

Version 1.2

PART 1: PLEASE REFER TO ATTACHED DOCUMENTS - OVERVIEW & FORMAT SAMPLES

PART 2: PRODUCTS

Division 28 – Electric Safety and Security

Level 1 - 28.20.00 – Video Surveillance

Level 2 - 28.21.00 – Surveillance Cameras

Level 3 - 28.21.13 – IP Cameras

Manufacturer

- IDIS Co., Ltd.
IDIS Tower, 344 Pangyo-ro, Bundang-gu
Seongnam-si, Gyeonggi-do, 13493, Korea
Tel: 	+82 31 723 5400
Fax: 	+82 31 723 5100

General

Product Description

The DC-D4538RA is a 5-megapixel AI IR dome camera designed for professional indoor surveillance applications. Featuring IDIS Deep Learning Analytics (IDLA) and LightMaster NIR technology, the camera combines intelligent video analytics with low-light imaging capabilities. This model is NDAA- and TAA-compliant.

The camera is equipped with a 1/2.8" progressive scan CMOS sensor and a 2.7–13.5mm motorized vari-focal lens with an aperture range of F1.4–F3.2, supporting remote focus and zoom adjustment. It delivers a maximum resolution of 2592 x 1944 at 30 images per second, including operation with True WDR at 120dB. H.265, H.264 Main Profile, and MJPEG compression are supported, together with IDIS Intelligent Codec, CBR/VBR bitrate control for H.265 and H.264, and quadruple video streaming for efficient bandwidth and storage use.

True Day/Night operation with an IR cut filter and six integrated IR LEDs provides night-time illumination up to 40 meters (131.2 ft). Minimum illumination is 0.13 lux at F1.4 in color mode and 0 lux in black-and-white mode with the IR LEDs activated. Image adjustment functions include exposure, white balance, sharpness, contrast, color, and brightness control. Additional imaging features include de-fog, horizontal and vertical mirroring, pivot, and privacy masking with up to eight zones.

Integrated IDLA provides object detection, intrusion detection, loitering detection, line crossing detection, and face detection, with object metadata for humans, vehicles, and faces. Additional event functions include video motion detection, audio detection, and active tampering alarms. Event notifications are available through remote software and email with images, and the camera supports audio alarms.

The camera supports microSD/SDHC/SDXC edge storage up to 512GB with Smart Failover, together with an NLTSrec recording buffer of up to 60MB for handling video transmission delays. It supports DirectIP 2.0 and ONVIF Profile S/T for integration with compatible surveillance systems. Interfaces include one alarm input, one alarm output, line-level audio input and output, and a built-in microphone, with two-way audio communication. Power is supplied through 12VDC or PoE compliant with IEEE 802.3af Class 3, with power consumption specified at 12W for DC operation and 9.5W for PoE operation.

General Specification

- The IP camera shall be equipped with 5 Megapixel 1/2.8” CMOS Sensor.

- The IP camera shall be equipped with 2.7mm – 13.5mm motorized vari-focal lens, F1.4 – F3.2.

- The IP camera shall be a true day/night camera with a mechanical filter for low light performance.
The filter can be switched remotely, or automatically via a light level sensor or contact input (ICR).

- The IP camera shall have wide dynamic range compensation (True WDR) for improved video quality in high-contrast situations (120 dB).

- The IP camera shall be equipped with 6ea Infrared LEDs with range up to 40m /131.2ft.

- The IP camera shall support DC-Iris.

- The IP camera shall utilize 2DNR/3DNR (Dynamic Noise Reduction) technology to reduce the bitrate and storage requirements by removing noise artifacts.

- The IP camera shall be equipped with 10/100 Base-T, auto-sensing, half/full duplex, RJ-45 Ethernet connection.

- The IP camera shall support industry standard Power over Ethernet (PoE) IEEE 802.3af, Class 3 to supply power to the camera over the network and 12VDC input.

- Using IDIS NLTSrec(Non-Linear Time Shifting recording) technology, the IP camera can store the recording data to the internal recording memory buffer (60MB) in camera if there is a delay in data transmission due to the instantaneous load of the recorder or network, and then transmits the stored data to IDIS recorder safely.

- The IP camera shall deliver maximum video resolution of 2592x1944 at rates up to 30ips (images per second).

- The IP camera shall provide network connection using H.265, H.264 and M-JPEG compression.

- The IP camera shall support quadruple streams in DirectIP 2.0 protocol mode.

- The IP camera shall conform to the ONVIF Profile S/T.

- The IP camera shall be equipped with embedded web server (IDIS Web) which works independently using a Web Browser with ActiveX plug-in.

- The IP camera shall have Digest authentication, Password Protection, User access log, IP Filtering, IEEE802.1x(EAP-TLS), Chained Fingerprint, SSL Encryption and HTTPS Encryption for greater security.

- The IP camera shall have network bandwidth limitation and MAT features for more efficient use of network bandwidth.

- The IP camera shall have Easy network access via UPnP (Universal Plug and Play) function and embedded mDNS (Multicast DNS) protocol.

- The IP camera shall have Intelligent Video Analysis (VA):

- Object Metadata: Human, Vehicle, Face

- IDLA: Object Detection, Intrusion, Loitering, Line Crossing, Face Detection

- ETC: Video Motion Detection, Active Tampering Alarm

Protocol Specification: DirectIP 2.0

- The IP camera shall have DirectIP 2.0 mode.

- DirectIP 2.0 protocol shall provide easy connection to DirectIP NVR for automatic discovery and video streaming configuration.

- DirectIP 2.0 shall provide the compatibility with IDIS Solution Suite VMS or ONVIF for third-party software solutions.

- DirectIP 2.0 shall support camera can be linked to IDIS software solution such as IDIS Center and IDIS Solution Suite, or 3rd party solution while it is being connected to a DirectIP NVR.

- DirectIP 2.0 camera shall be compatible with DirectIP 1.0 NVR as well as DirectIP 2.0 NVR.

- DirectIP 2.0 camera shall be unavailable for No-password login when connecting to DirectIP 2.0 NVR and IDIS Software Solutions.

- DirectIP 2.0 protocol shall provide Quadruple streams.

- DirectIP 2.0 protocol shall support H.264 and H.265 and MJPEG compression.

Technical Specification

Video Specification

- Image Sensor: 1/2.8” CMOS

- Maximum Resolution: 2592x1944

- Scanning Mode: Progressive Scan

- Lens Type: Motorized Vari-focal (f=2.7 – 13.5mm, F1.4 – 3.2)

- Iris Control: DC-Iris

- Angular Field of View (H: Horizontal, V: Vertical, D: Diagonal):

[4:3 mode]

Wide : 101.2º(H) 72.5º(V) 137.4º(D)

Tele : 30.4º(H) 22.8º(V) 38º(D)

[16:9 mode]

Wide : 101.2º(H) 53.3º(V) 121.6º(D)

Tele : 30.4º(H) 17º(V) 34.7º(D)

- Pan/Tilt Range: Pan: -175° ~ 175°, Tilt: 0° ~ 60°, Rotate: -177° ~ 177°

- Minimum Illumination:

  - COLOR: 0.13 lux @ F1.4

  - B/W : 0 lux  (IR LED ON)

- S/N Ratio: More than 45 dB

- Maximum Frame Rate:

  - [4:3 mode]: 30ips : 2592 x 1944(WDR)

  - [16:9 mode]: 30ips : 2592 x 1456(WDR)

- Video Resolution:

  - [4:3 mode]: 2592x1944, 1920x1440, 1280x960x 640x480

  - [16:9 mode]: 2592x1456, 1920x1080, 1280x720, 640x360

- Video Compression: H.265, H.264 (MP), MJPEG

- Video Compression Level: 4 levels: Basic, Standard, High, Very High

- Intelligent Codec is supported.

- Multi-Video Streaming: Quadruple streams

- Dynamic Range: 120dB

- True Day & Night: Yes (ICR)

- IR Distance (The number of LEDs, IR wavelength): 40m (131.2ft.) (6ea)

- Intelligent Video Analytic:

Object Metadata: Human, Vehicle, Face

IDLA: Object Detection, Intrusion, Loitering, Line Crossing, Face Detection

ETC: Video Motion Detection, Active Tampering Alarm

Audio Specification

- Audio Compression Algorithm: OPUS, ADPCM 16K, G.726 (16kHz), G.711 u-Law (8kHz), G.711 a-Law

- Audio Input / Output: 1(Line-in) + 1(Built-in Mic) / 1(Line-out)

- Two-way Audio Communication: Yes

- Pre-recorded Voice Alert(Audio Alarm): On / Off

Network Specification

- Port: RJ-45 10/100 Base-T 1 port

- Network Protocols: DirectIP 2.0 Protocol, IPv4, IPv6, RTP/RTSP/TCP, RTP/RTSP/HTTP/TCP,

- Streaming Mode: Quadruple Streaming

Security Specification

- Digest authentication, Password Protection, User access log, IP Filtering, IEEE802.1x(EAP-TLS), Chained Fingerprint, SSL Encryption, HTTPS Encryption

- Maximum Concurrent Session: 10 sessions shared across Admin, Watch, and Search, with a maximum of 1 Search session.

Alarm and Event Specification

- Alarm Input / Output: 1 / 1

  - Alarm Input: TTL, NC/NO Programmable, 4.3V(NC) or 0.3V(NO) threshold, 5V DC

  - Mechanical or electrical switches can be wired to the Alarm-In and GND connectors. The maximum voltage should not exceed 5V.

  - Alarm Output: 1 TTL open collector, 30mA @ 5 VDC

- Trigger Events: Motion Detection, Alarm in, Audio detection, Tampering, Object Detection, Intrusion, Loitering, Line Crossing, Face Detection

- Event Notification: Remote S/W, Email (with Image)

  - Encryption Type: SSL

Environmental Specification

- Operating Temperature: -10°C ~ +50°C (+14°F ~ +122°F)

*Starting up at above 0°C (32°F)

- Operating Humidity: 0% to 90% non-condensing

Electrical Specification

- Power Source: PoE (IEEE 802.3af class 3), 12VDC

- Power Consumption:

    - PoE, IEEE 802.3af Class 3, 9.5W

    - 12V=, 1A, 12W

- Regulatory Approvals: FCC, CE, KC

Mechanical Specification

- Dimensions (Ø x H): Ø122 x 103.4mm

- Unit Weight: 0.35kg (0.77lb)

- Version History

| Version | Writer | Revision Date | Remarks |
| --- | --- | --- | --- |
| 1.0 | Tech support | July. 29, 2022 | Initial Release |
| 1.1 | Tech support | Feb. 17, 2025 | Update |
| 1.2 | GT Team | Oct. 22. 2026 | Updated the description and specifications. |